## loads
bus_id | name | vn_kv | population | demand_share | power_p_mw | power_q_mvar | power_s
0 | La Paz | 230 | 2926996 | 0.2516 | 3041.8854 | 999.8194 | 3201.9847
1 | Pando | 230 | 154355 | 0.013268 | 160.4137 | 52.7254 | 168.8565
2 | Beni | 230 | 480308 | 0.041287 | 499.1609 | 164.0662 | 525.4325
3 | Oruro | 230 | 551116 | 0.047374 | 572.7482 | 188.2532 | 602.8929
4 | Cochabamba | 230 | 2028639 | 0.17438 | 2108.2664 | 692.9537 | 2219.2278
5 | Santa Cruz | 230 | 3370059 | 0.28969 | 3502.3394 | 1151.1633 | 3686.673
6 | Potosi | 115 | 901555 | 0.077497 | 936.9425 | 307.9581 | 986.2553
7 | Chuquisaca | 230 | 637013 | 0.054757 | 662.0168 | 217.5944 | 696.8598
8 | Tarija | 230 | 583330 | 0.050143 | 606.2267 | 199.2571 | 638.1333

## buses
bus_id | name | vn_kv | geodata
0 | La Paz | 230 | -16.5, -68.15
1 | Pando | 230 | -11.02671, -68.76918
2 | Beni | 230 | -14.83333, -64.9
3 | Oruro | 230 | -17.98333, -67.15
4 | Cochabamba | 230 | -17.3895, -66.1568
5 | Santa Cruz | 230 | -17.78629, -63.18117
6 | Potosi | 115 | -19.58361, -65.75306
7 | Chuquisaca | 230 | -19.03332, -65.26274
8 | Tarija | 230 | -21.53549, -64.72956
9 | trafo02 | 115 | -16.5, -68.15
10 | trafo20 | 115 | -14.83333, -64.9
11 | trafo36 | 115 | -17.98333, -67.15
12 | trafo68 | 230 | -21.53549, -64.72956
13 | trafo64 | 115 | -17.3895, -66.1568
14 | trafo67 | 115 | -19.03332, -65.26274

## gen
gen_id | name | bus_id | p_mw_100 | p_mw_95 | p_mw_90 | p_mw_85 | p_mw_80 | p_mw_75 | p_mw_70 | p_mw_65 | p_mw_60 | p_mw_55 | p_mw_50 | p_mw_45 | p_mw_40 | p_mw_35 | p_mw_30 | p_mw_25 | p_mw_20 | p_mw_15 | p_mw_10 | p_mw_5
0 | La Paz | 0 | 3769.3757 | 3631.3716 | 3493.3676 | 3355.3636 | 3217.3596 | 3079.3555 | 2941.3515 | 2803.3475 | 2665.3434 | 2527.339 | 2389.335 | 2251.331 | 2113.327 | 1975.323 | 1837.319 | 1699.315 | 1561.311 | 1423.307 | 1285.303 | 1147.299
1 | Pando | 1 | 24.048 | 22.9956 | 21.9432 | 20.8908 | 19.8384 | 18.786 | 17.7336 | 16.6812 | 15.6288 | 14.5764 | 13.524 | 12.4716 | 11.4192 | 10.3668 | 9.3144 | 8.262 | 7.2096 | 6.1572 | 5.1048 | 4.0524
2 | Beni | 2 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
3 | Oruro | 3 | 729.275 | 717.3112 | 705.3475 | 693.3837 | 681.42 | 669.4562 | 657.4925 | 645.5287 | 633.565 | 621.6013 | 609.6375 | 597.6738 | 585.71 | 573.7463 | 561.7825 | 549.8188 | 537.855 | 525.8913 | 513.9275 | 501.9638
4 | Cochabamba | 4 | 4240.0822 | 4072.3229 | 3904.5636 | 3736.8043 | 3569.045 | 3401.2857 | 3233.5264 | 3065.7671 | 2898.0078 | 2730.249 | 2562.489 | 2394.73 | 2226.971 | 2059.211 | 1891.452 | 1723.693 | 1555.933 | 1388.174 | 1220.415 | 1052.656
5 | Santa Cruz | 5 | 4249.098 | 4112.7431 | 3976.3882 | 3840.0333 | 3703.6784 | 3567.3235 | 3430.9686 | 3294.6137 | 3158.2588 | 3021.904 | 2885.549 | 2749.194 | 2612.839 | 2476.484 | 2340.129 | 2203.775 | 2067.42 | 1931.065 | 1794.71 | 1658.355
6 | Potosi | 6 | 1197.1829 | 1160.7884 | 1124.3939 | 1087.9994 | 1051.6049 | 1015.2104 | 978.8159 | 942.4214 | 906.0269 | 869.6324 | 833.2379 | 796.8434 | 760.4489 | 724.0544 | 687.6599 | 651.2654 | 614.8709 | 578.4764 | 542.0819 | 505.6874
7 | Chuquisaca | 7 | 682.7824 | 675.2824 | 667.7824 | 660.2824 | 652.7824 | 645.2824 | 637.7824 | 630.2824 | 622.7824 | 615.2824 | 607.7824 | 600.2824 | 592.7824 | 585.2824 | 577.7824 | 570.2824 | 562.7824 | 555.2824 | 547.7824 | 540.2824
8 | Tarija | 8 | 496.3281 | 490.966 | 485.6039 | 480.2417 | 474.8796 | 469.5174 | 464.1553 | 458.7932 | 453.431 | 448.0689 | 442.7068 | 437.3446 | 431.9825 | 426.6203 | 421.2582 | 415.8961 | 410.5339 | 405.1718 | 399.8097 | 394.4475

## lines
from_bus | to_bus | length_km | cable_type | bundle_no | Dm | A | Rb | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | max_i_ka | cables | voltage | location
2 | 0 | 477 | 0 | 2 | 12 | 0 | 0 | 0.03806 | 0.22244 | 7.9896e-06 | 1.51 | 3 | 115 | overhead
0 | 3 | 286 | 0 | 2 | 12 | 0 | 0 | 0.02953 | 0.2139 | 7.8015e-06 | 1.815 | 3 | 230 | overhead
0 | 4 | 298 | 0 | 2 | 12 | 0 | 0 | 0.02953 | 0.2139 | 7.8015e-06 | 1.815 | 3 | 230 | overhead
3 | 4 | 138 | 0 | 2 | 12 | 0 | 0 | 0.02953 | 0.2139 | 7.8015e-06 | 1.815 | 3 | 230 | overhead
4 | 5 | 401 | 0 | 2 | 12 | 0 | 0 | 0.02953 | 0.2139 | 7.8015e-06 | 1.815 | 3 | 230 | overhead
5 | 2 | 538 | 0 | 2 | 12 | 0 | 0 | 0.02953 | 0.2139 | 7.8015e-06 | 1.815 | 3 | 230 | overhead
4 | 6 | 365 | 0 | 2 | 12 | 0 | 0 | 0.03806 | 0.22244 | 7.9896e-06 | 1.51 | 3 | 115 | overhead
3 | 6 | 329 | 0 | 2 | 12 | 0 | 0 | 0.03806 | 0.22244 | 7.9896e-06 | 1.51 | 3 | 115 | overhead
6 | 7 | 155 | 0 | 2 | 12 | 0 | 0 | 0.03806 | 0.22244 | 7.9896e-06 | 1.51 | 3 | 115 | overhead
4 | 7 | 246 | 0 | 2 | 12 | 0 | 0 | 0.02953 | 0.2139 | 7.8015e-06 | 1.815 | 3 | 230 | overhead
2 | 1 | 1123 | 0 | 2 | 12 | 0 | 0 | 0.02953 | 0.2139 | 7.8015e-06 | 1.815 | 3 | 230 | overhead
6 | 8 | 328 | 0 | 2 | 12 | 0 | 0 | 0.02953 | 0.2139 | 7.8015e-06 | 1.815 | 3 | 230 | overhead
use this to switch between cable types
cable used: |  | Cable type | Area | Resistance at 25 | Inductance | Capacitance | max_i_ka | kv | height (m) | diameter (mm) | radius (m) | permitivity | capacitance (F/m) | nf/km
page 3 and 4 from :https://www.elandcables.com/media/38193/acsr-astm-b-aluminium-conductor-steel-reinforced.pdf | OVERHEAD | BLUEBIRD | 1181.6 | 0.02953 | 0.2139 | 1e-09 | 1.815 | 230 | 7.6 | 12.2 | 0.0061 | 8.85e-12 | 7.8e-12 | 7.8e-06
|  | FALCON | 908.6 | 0.03806 | 0.22244 | 1e-09 | 1.51 | 115 | 6.9 | 13.1 | 0.00655 | 8.85e-12 | 7.99e-12 | 7.99e-06
| current ones | Rail | 483.8 | 0.06201 | 0.2454 | 1e-09 | 1.09 | 230 | 7.6 | 7.41 | 0.003705 | 8.85e-12 | 7.29e-12 | 7.29e-06
|  | Ibis | 201.3 | 0.1444 | 0.2739 | 1e-09 | 0.635 | 115 | 6.9 | 7.32 | 0.00366 | 8.85e-12 | 7.37e-12 | 7.37e-06

## trafos
bus_id | bus_name | from_bus | to_bus | V_in | V_out | S-MVA
9 | trafo02 | 0 | 9 | 230 | 115 | 40
10 | trafo20 | 10 | 2 | 115 | 230 | 40
11 | trafo36 | 3 | 11 | 230 | 115 | 40
12 | trafo68 | 6 | 12 | 115 | 230 | 40
13 | trafo64 | 13 | 4 | 115 | 230 | 40
14 | trafo67 | 14 | 7 | 115 | 230 | 40

## Generation capacity data
Region | 100% | 95% | 90% | 85% | 80% | 75% | 70% | 65% | 60% | 55% | 50% | 45% | 40% | 35% | 30% | 25% | 20% | 15% | 10% | 5%
La Paz | 3769.3757 | 3631.3716 | 3493.3676 | 3355.3636 | 3217.3596 | 3079.3555 | 2941.3515 | 2803.3475 | 2665.3434 | 2527.339 | 2389.335 | 2251.331 | 2113.327 | 1975.323 | 1837.319 | 1699.315 | 1561.311 | 1423.307 | 1285.303 | 1147.299
Pando | 24.048 | 22.9956 | 21.9432 | 20.8908 | 19.8384 | 18.786 | 17.7336 | 16.6812 | 15.6288 | 14.5764 | 13.524 | 12.4716 | 11.4192 | 10.3668 | 9.3144 | 8.262 | 7.2096 | 6.1572 | 5.1048 | 4.0524
Beni | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
Oruro | 729.275 | 717.3112 | 705.3475 | 693.3837 | 681.42 | 669.4562 | 657.4925 | 645.5287 | 633.565 | 621.6013 | 609.6375 | 597.6738 | 585.71 | 573.7463 | 561.7825 | 549.8188 | 537.855 | 525.8913 | 513.9275 | 501.9638
Cochabamba | 4240.0822 | 4072.3229 | 3904.5636 | 3736.8043 | 3569.045 | 3401.2857 | 3233.5264 | 3065.7671 | 2898.0078 | 2730.249 | 2562.489 | 2394.73 | 2226.971 | 2059.211 | 1891.452 | 1723.693 | 1555.933 | 1388.174 | 1220.415 | 1052.656
Santa Cruz | 4249.098 | 4112.7431 | 3976.3882 | 3840.0333 | 3703.6784 | 3567.3235 | 3430.9686 | 3294.6137 | 3158.2588 | 3021.904 | 2885.549 | 2749.194 | 2612.839 | 2476.484 | 2340.129 | 2203.775 | 2067.42 | 1931.065 | 1794.71 | 1658.355
Potosi | 1197.1829 | 1160.7884 | 1124.3939 | 1087.9994 | 1051.6049 | 1015.2104 | 978.8159 | 942.4214 | 906.0269 | 869.6324 | 833.2379 | 796.8434 | 760.4489 | 724.0544 | 687.6599 | 651.2654 | 614.8709 | 578.4764 | 542.0819 | 505.6874
Chuquisaca | 682.7824 | 675.2824 | 667.7824 | 660.2824 | 652.7824 | 645.2824 | 637.7824 | 630.2824 | 622.7824 | 615.2824 | 607.7824 | 600.2824 | 592.7824 | 585.2824 | 577.7824 | 570.2824 | 562.7824 | 555.2824 | 547.7824 | 540.2824
Tarija | 496.3281 | 490.966 | 485.6039 | 480.2417 | 474.8796 | 469.5174 | 464.1553 | 458.7932 | 453.431 | 448.0689 | 442.7068 | 437.3446 | 431.9825 | 426.6203 | 421.2582 | 415.8961 | 410.5339 | 405.1718 | 399.8097 | 394.4475